| Trade of Sheet Metalwork |
| --- |
| Module 5: | Ductwork |
| Unit 1: | Cylinder with Damper, Square & Rectangular Duct |
|  | Phase 2 |

Table of Contents

List of Figures	6

List of Tables	7

Document Release History	8

Module 5 – Ductwork	9

Unit 1 – Cylinder with Damper, Square & Rectangular Duct	9

Learning Outcome:	9

Key Learning Points:	9

Training Resources:	10

Key Learning Points Code:	10

Lockform Machine	12

Cross-Sectional Type	12

Longitudinal Joints/Seams	17

Ductwork	21

Standing Seam	21

Dovetail Seam	22

Slip Joints	23

“C” Cleats	23

“S” Cleats	24

Peened Joint	24

Allowance for Peened Joint	25

Abbreviations used in Ductwork	26

DW/144	26

Dampers	26

Noise	26

Regulating Dampers	27

General	27

Balancing Damper	27

Control Damper	27

Types of Airflow Control Damper	27

Single-Blade Dampers (Single or Double Skin)	27

Multi-Blade Dampers (Single or Double Skin) Parallel or Opposed Blade	28

Iris Dampers	28

Backdraft Dampers	28

Hit and Miss Dampers	28

Slide and Blast Gate Dampers	28

Construction	29

Materials	29

Dampers used in Low and Medium Pressure Systems	29

Dampers used in High Pressure Systems	29

Proprietary Types of Damper	29

Damper Casings	30

Installation	30

Fire Dampers	31

General	31

Types of Fire Dampers	31

Folding Curtain	31

Single Blade	31

Multi-Blade	32

Intumescent	32

Materials and Construction	33

Air Leakage	33

Location	33

Provision for Expansion	33

Installation	33

Smoke Dampers	34

General	34

Types of Smoke Damper	34

Single Blade	34

Multi-Blade	34

Materials and Construction	34

Air Leakage	34

Installation	34

Combination Smoke and Fire Dampers	35

General	35

Types of Combination Smoke and Fire Damper	35

Single Blade	35

Multi-Blade	35

Materials and Construction	36

Air Leakage	36

Installation	36

Internal Duct Linings	37

General	37

Lining Application Considerations	37

Circular Ducts	37

Cleaning and Maintenance	37

Thermal Insulation	38

Standard Component Drawings and Abbreviations	38

Self Assessment	44

Answers to Questions 1-4. Module 5.Unit 1	46

Index	48

# List of Figures

Figure 1 - Round Duct with Damper	11

Figure 2 - Angle and Band Iron Edge	12

Figure 3 - Forming a Dovetail Seam	13

Figure 4 - Standing Seam	13

Figure 5 - Steps in Making a Hand Seam	14

Figure 6 - Steps in Forming a Government Clip	14

Figure 7 - Making a Double Seam	14

Figure 8 - Steps in Making a Bottom Double Seam	15

Figure 9 - S and Drive Clips used to Join Duct Sections	15

Figure 10 - S Clips used to Join Sheet Metal Pieces Covering a Wall	16

Figure 11 - Steps in Assembling a Drive Clip Seam	16

Figure 12 - Pittsburgh Seams can be Formed on Curves	17

Figure 13 - Slip Joint Seam	17

Figure 14 - Proper and Improper Joining of Slip Joint Seams	18

Figure 15 - Steps in forming the Pittsburgh Lock	18

Figure 16 – Common Seams used in Sheet Metal Work	19

Figure 17 - Steps in Forming a Grooved Seam	20

Figure 18 - Steps in Forming the Pittsburgh Seam	20

Figure 19 - Lockform Joint	21

Figure 20 - Standing Seam	21

Figure 21 - Dovetail Seam	22

Figure 22 - Slip Joints	23

Figure 23 – “C” Cleat	23

Figure 24 - "S" Cleats	24

Figure 25 - Joggled Lap Seam	24

Figure 26 - Corner Seam with Lap on the Outside	25

Figure 27 - 6mm Paned-Down Joint	25

Figure 28 – Allowance for Peened Joint	25

Figure 29 – Alternative Provision for Expansion	32

# List of Tables

Table 1 - Standard Component Drawings – Rectangular	41

Table 2 - Standard Abbreviations	43

# Document Release History

| Date | Version | Comments |
| --- | --- | --- |
| 10/01/07 | First draft |  |
| 09/04/14 | 2.0 | SOLAS transfer |

# Module 5 – Ductwork

## Unit 1 – Cylinder with Damper, Square & Rectangular Duct

Duration – 21 Hours

### Learning Outcome:

By the end of this unit each apprentice will be able to:

Read and interpret HVAC drawings

Sketch ductwork

Use the lockform machine

Produce and fabricate a cylinder with slip joint (big end and small end) and double seam joint (machine joint)

Produce and fabricate a rectangular duct with cross breaking and propriety flanges

Produce and fabricate a square duct with damper and use 'S' and 'C' cleats

### Key Learning Points:

| H Rk | Set, use and operation of lockform machine. |
| --- | --- |
| Rk | Design and position of joints on ductwork and fittings. |
| Rk Sk | Marking-out/fabrication techniques. |
| Rk Sk | Tacking and closing procedure of joints on ductwork. |
| Rk | Damper types and fitting arrangements. |
| Rk | (DW144) Ductwork specifications and standards. |
| D Rk | Layout of HVAC drawings, abbreviations, use of scale rule, sketching. |
| Rk Sk | Ductwork design and quality. |
| Rk | Design and use of cleats. |
| M | Calculate allowance for double seam and lockform joints and area/weight of metal in ductwork. |
| Sc | Work, energy, power and friction, density/specific gravity. |

### Training Resources:

Toolkit

0.6mm galvanised steel

DW 143, DW/TM2. TR.7

DW 144. DW.171.BS 5970:2001

Workshop drawings

Live example

Scale rule. (metric, imperial)

Refer to reference library

Safety equipment and protective clothing

Tools and machinery/equipment

### Key Learning Points Code:

M = Maths	           D= Drawing     RK = Related Knowledge Sc = Science

P = Personal Skills	Sk = Skill	   H = Hazards

Figure 1 - Round Duct with Damper

# Lockform Machine

The allowance for the lockform machine is usually 25mm for a small one and 35mm for the bigger one. There is also a small edge ranging in size from 6mm to 10mm which slots into the larger end. Some machines with age may deviate from the manufacturer’s recommended allowance so trial and error may apply. Sharp edges need to be handled safely when using these machines. Gloves are needed.

## Cross-Sectional Type

- Flanging: Mez type and ordinary angle (iron)

- Slip joints normally 25mm – 50mm in size

- S and C cleats

- Hand seams

- Flexible joints; here improvement may happen as at the fan connected to the duct.

- Angle iron edge, band iron edge

Figure 2 - Angle and Band Iron Edge

Figure 3 - Forming a Dovetail Seam

Figure 4 - Standing Seam

Some joints may fall into both categories of joint, i.e. cross-sectional and longitudinal.

Figure 5 - Steps in Making a Hand Seam

Figure 6 - Steps in Forming a Government Clip

Figure 7 - Making a Double Seam

Figure 8 - Steps in Making a Bottom Double Seam

Figure 9 - S and Drive Clips used to Join Duct Sections

Figure 10 - S Clips used to Join Sheet Metal Pieces Covering a Wall

Figure 11 - Steps in Assembling a Drive Clip Seam

## Longitudinal Joints/Seams

The most important thing about a joint is it does not leak. Whichever joint is used it may have to be sealed by a gasket or a sealant like mastic or even soldered. Strength and durability are also very important. It is therefore advisable to be familiar with the specifications for the job. The apprentice should have some knowledge of the manual DW/144 and have a copy at his disposal for the reasons just stated.

Figure 12 - Pittsburgh Seams can be Formed on Curves

Figure 13 - Slip Joint Seam

Figure 14 - Proper and Improper Joining of Slip Joint Seams

Figure 15 - Steps in forming the Pittsburgh Lock

Figure 16 – Common Seams used in Sheet Metal Work

Figure 17 - Steps in Forming a Grooved Seam

Figure 18 - Steps in Forming the Pittsburgh Seam

The Pittsburgh lock is also known as the lockform and the grooved joint/seam as the double edged joint seam.

These two seams are the more popular of the above seams. The following pages have more detail for the more commonly used joints in ductwork.

# Ductwork

For ducting the most common joint is the lockform. The allowance for this varies with the machine - 35mm and 25mm are common. The lockform is a longitudinal seam as is a groove joint. The lockform or Pittsburgh lock is always positioned on a corner. Groove seams are rarely used in metal heavier than 20 gauge.

Figure 19 - Lockform Joint

## Standing Seam

Standing seams are used on large site ducting and of sheets of metal to connect and stiffen the metal. This joint eliminates the need for angle iron reinforcement.

The seam comes in various sizes and is secured with rivets or bolts at intervals.

Figure 20 - Standing Seam

## Dovetail Seam

A dovetail seam is used to connect a round pipe to a square or rectangular duct. In construction it consists of a series of tabs cut into the end of the pipe, with every other tab bent out at a 90° angle. The usual size for these cuts is about 3/8" wide and 3/8" deep. The size of these tabs will vary with the size of the pipe.

Figure 21 - Dovetail Seam

In the erection of ductwork, cross seam connections take the following form:

- Slip joints (solid or "pop" riveted).

- Angle iron flanges (bolted) and mez flanging.

- S & C cleats (commonly known as S & Drive cleats) and where extra strength is required.

- Standing "S" cleats (used with drive cleats) and where extra strength is required.

- Government/cut clip (not widely used in this country but very popular in the USA).

The type of connector used is determined by the size of the duct, strength required, and the type of application. The more popular types used in this country are items 1, 2, and 3 above, but a lot depends on the specification for a particular contract.

## Slip Joints

Figure 22 - Slip Joints

The usual allowance for slip joints are 25mm, 38mm or 50mm.

Slip joints are a popular way of joining square or cylindrical ducting. On cylindrical ducting the end of the pipe is usually swaged about 1½" to 2" away from the end. It is then crimped (reduced) to sit into the end of the next section of ducting. Another way to do it is to make one end of the pipe or duct smaller in diameter than the other end. On square or rectangular ducting, the end of the duct is notched on the corners to allow it to slip into the end of the next section of ducting. It is then sealed and riveted. Slip joints are usually used on small size square or rectangular ducting.

## “C” Cleats

"C" Cleat (or drive cleat as it is known). This cleat is generally used in connection with S cleats for connecting cross seams on ducts. It is generally used on the short side of the duct.

Figure 23 – “C” Cleat

## “S” Cleats

"S" Cleats are used in conjunction with "C" or drive cleats on the cross seams of ductwork. You may have a plain "S" cleat, hemmed "S" cleat, or the standing "S" cleat where extra strength is required.

Figure 24 - "S" Cleats

## Peened Joint

Peened joint is also known as paned joint. The paned or peened joint is used as a simple means of attaching a bottom to an article of cylindrical or conical shape, and it can also be used to secure the segments together in a lobster back bend. The allowance for this joint can very slightly from craftsman to craftsman.

Figure 25 - Joggled Lap Seam

Figure 26 - Corner Seam with Lap on the Outside

Figure 27 - 6mm Paned-Down Joint

W = 6mm

X = 6mm - 0.5mm = 5.5mm

Y = 6mm + 0.5mm = 6.5mm

Total: 3W or 18mm

(12mm + 6mm)

## Allowance for Peened Joint

A general method would be to leave a single edge on one side of the pattern (this would be the size of the peened joint) and on the other of the pattern leave a double edge (this would be twice the size of the peened joint). On making the paned joint, the thickness of material will have to be taken into consideration to finish the joint properly.

Figure 28 – Allowance for Peened Joint

## Abbreviations used in Ductwork

AF 		= 	Airflow

VCD 		= 	Volume Control Damper

CFM 		= 	Cubic feet per minute

F.P.M. 	= 	Feed per minute

TA 		= 	To above

FD 		= 	Fire Damper

HVAC 		= 	Heating, Ventilation Air Conditioning

AHU 		= 	Air Handling Unit

DIA 		= 	Diameter

I.D. 	 	= 	Inside Diameter

## DW/144

Ductwork/144 the name given to the design specifications approved by the Heating & Ventilation Association. It makes reference to bend radii, rivet spacings, cross checks on ducts and what size mez flange is required. Its idea is to raise quality and have a standard which no contractor should fall below.

## Dampers

There are three types to be aware of:

- Fire damper, which closes if the temperature rises too high. The reason for this high temperature may be a fire. The idea is to prevent air (oxygen) feeding the fire;

- Volume control damper, which may be closed partially or fully by mechanical means to reduce or stop air flow;

- Smoke damper, which restricts the speed of smoke.

## Noise

To reduce noise in duct systems a flexible connection may be used when connecting fans to the duct. Baffles, which reduce noise, may also be fitted. The inside of the duct may also be lagged which will help insulation as well as noise reduction. Sharp bends should not be in the system. If they already are, their turning vanes should be installed to reduce noise.

The following pages refer to the DW/144 standards concerning dampers and they also give examples of component drawings and abbreviations.

# Regulating Dampers

## General

Balancing dampers and control dampers are elements inserted into an air distribution system, or elements of an air distribution system. Balancing dampers permit modification of the air resistance of the system and consequently changing of the airflow rate. Control dampers control the airflow rate and in addition provide low leakage closure of the airflow.

The designer shall specify damper locations and select the damper type, as defined in “Types of Airflow Control Damper” below, appropriate to the airflow, pressure and acoustic characteristics.

### Balancing Damper

To achieve the required distribution of air in the ductwork system at inlets and/or outlets. For this purpose, the damper blades are set and locked manually in any required position between fully open and fully closed.

### Control Damper

To secure dynamic control of the air flow in the ductwork system. In this function, the damper will always be power - actuated and may require to be modulated between fully open and fully closed, and to be capable of taking up any position between these extremes. In the fully open position, the damper should have a minimum pressure drop. In the fully closed position, it will not necessarily achieve a complete shut off.

## Types of Airflow Control Damper

Air flow dampers of various types are available for specific purposes as follows.

### Single-Blade Dampers (Single or Double Skin)

Single-blade dampers shall consist of a single pivoted blade contained within a casing or section of ductwork. The blade shall be adjustable through a nominal 90° angle by means of a quadrant or similar operating mechanism. Where automatic control of the damper is required the spindle shall be extended to enable a powered actuator to be mounted.

Single-blade dampers (single-skin section) shall have a maximum duct width of 300 mm and a maximum duct height of 300 mm for rectangular ducts; and for circular ducts a maximum diameter of 315 mm.

Single-blade dampers (double-skin section) are suitable for use in rectangular ducts, and shall have a maximum duct width of 1250 mm and a maximum height of 300 mm.

### Multi-Blade Dampers (Single or Double Skin) Parallel or Opposed Blade

Multi-blade dampers shall consist of a number of pivoted blades contained within a casing. The blades shall be adjustable through a nominal 90° angle simultaneously by interconnected linkage or gears, connected to a quadrant or similar operating mechanism. Where automatic control of the damper is required a spindle shall be extended to enable a powered actuator to be mounted.

There is no restriction on the size of duct in which multi-blade dampers or damper assemblies may be used. Where dampers are required for blade lengths in excess of 1250 mm, the blades should be suitably reinforced or supported. No individual damper blade should exceed 200 mm in width.

### Iris Dampers

Iris dampers shall consist of a number of radially inter-connected blades which open or close within a casing with duct connection spigots. The blades shall be simultaneously adjusted by a quadrant or similar operating mechanism.

Iris dampers should be installed as specified by the manufacturer's operating and installation instructions, where the product is unidirectional with regard to airflow.

Iris dampers are available for circular ducts only, in diameters up to 800 mm (It should be noted that the damper casing is approximately twice the diameter of the duct).

### Backdraft Dampers

Air pressure operated unidirectional rectangular (single or multi-blade) with adaptors if fitted to circular or oval ducts.

### Hit and Miss Dampers

Two parallel adjacent plates each with multiple openings sliding against each other. The openings are designed to provide 50% air volume flow rates when they fully coincide. Used for simple operations up to 400 mm longest side.

### Slide and Blast Gate Dampers

A damper used as a shut off facility, normally for use in circular ductwork with an external slide housing allowing a blade to be fully inserted to fully extended for maximum air flow.

Generally available in cast/pressed formats up to 355 mm diameter and normally used in industrial exhaust applications.

## Construction

### Materials

Dampers shall be constructed from steel, stainless steel, aluminium or synthetic materials.

All products should be protected against corrosion as necessary and supplied in a fully finished condition a specified by the designer.

### Dampers used in Low and Medium Pressure Systems

The following recommendations apply to dampers forming an integral part of ductwork with pressure classification A and B air leakage limits.

The dampers shall be constructed to prevent distortion and jamming in operation. The blades shall be sufficiently rigid to minimise movement when in the locked position.

The blades shall be securely fixed to the operating mechanism. Spindles shall be carried in either non-ferrous, synthetic or roller bearings. All balancing dampers shall have a locking device located on the outside of the case and shall give clear indication of the actual blade position. All penetrations of the duct shall be fitted with suitable seals where necessary.

### Dampers used in High Pressure Systems

Regulating dampers used in ductwork systems to pressure classification C shall meet the construction requirements specified in “Materials” and “Dampers used in Low and Medium Pressure Systems” above with operating mechanisms out of the airstream.

### Proprietary Types of Damper

The use of any specific type of proprietary damper shall be confirmed by the designer. In all cases, proprietary dampers shall meet the relevant requirements of this specification.

### Damper Casings

Duct damper casings shall be constructed to meet the minimum leakage limits specified for the ductwork system to which they are installed.

In order to apply the square meterage leakage calculation as detailed in DW/143 A practical guide to Ductwork Leakage Testing, the reference casing area shall be taken as the perimeter size of the damper multiplied by the equivalent length of one metre, for example an 800 mm x 400 mm duct damper shall have a surface area for casing leakage performance calculated as follows; [(2 x 0.8) + (2 x 0.4)] x 1 = 2.4m² casing area.

Other performance and rating test methods for dampers and valves are specified in IS05129 and BS/EN1751, and are referenced below:

- Leakage past a closed damper or valve		BS/EN 1751

- Flow rate/pressure 
requirement characteristics				BS/EN 1751

- Operational torque testing				BS/EN 1751

- Thermal transfer testing				BS/EN 1751

- Regenerated sound power levels			ISO 5129

## Installation

Dampers shall be installed in accordance with any relevant ISO, EN or British Standard, local building regulations and national codes of practice as well as the manufacturer's recommendations.

# Fire Dampers

## General

Dampers are required in air distribution systems for fire containment. Generally they are called for where ducts penetrate walls or floors which form fire compartmentation. The damper assembly should have a fire resistance rating equal to that of the fire barrier it penetrates and shall be fire tested and rated to the time/temperature curve of BS476 part 20 and 22.

## Types of Fire Dampers

Fire dampers of various types are available for specific purposes, as follows:

### Folding Curtain

Folding curtain fire dampers shall be constructed of a series of interlocking blades which fold to the top of the assembly permitting the maximum free area in the airway. The blades shall be held in the open position by means of a thermal release mechanism rated at 72°C ± 4°C.

The fire damper must be able to close against static air conditions when mounted in either the vertical or horizontal planes.

In the event of a signal from a remote sensor the fire damper blades shall be released and close the airway. A local excess temperature in the area of the fire damper shall, independent of any remote sensors, automatically release the blades and close the airway by means of the thermal release mechanism, electric solenoid or electromagnet.

### Single Blade

Single blade fire dampers shall consist of a single pivoted blade within a fire resistant case.

The blade shall be released from its open position by means of a thermal release mechanism rated at 72°C ± 4°C, electric solenoid, electromagnet(s) or other device.

The blade shall close the airway by means of anyone, or combination of, an eccentric pivot, balance weight(s) and/or spring(s), the spring element being incorporated within the damper or actuator mechanism.

The fire damper shall be able to operate in either or both the vertical and horizontal planes.

### Multi-Blade

Multi-blade fire dampers shall consist of a number of linked blades contained within a fire resistant case.

The blades shall be released from their open position by means of either a thermal release mechanism rated at 72°C ± 4°C, or by the force applied from electrical solenoid(s), electromagnet(s), electrical/pneumatic actuator or other device.

Figure 29 – Alternative Provision for Expansion

The blades shall close the airway by means of a spring(s), the spring element being incorporated within the damper or actuator mechanism.

The fire damper shall be able to operate in either or both the vertical and horizontal planes.

### Intumescent

Intumescent fire dampers shall be constructed from strips of intumescent material formed into a lattice or from honeycomb material covered with intumescent paint. The damper shall fully seal when heat or flame is applied from either side. Note these devices are generally used in door/partition low velocity applications.

## Materials and Construction

The damper shall be constructed from steel or stainless steel or other approved material. Steel products shall be protected against corrosion and supplied in a fully assembled condition as specified by the designer.

## Air Leakage

Fire damper casings shall meet the equivalent leakage performance standard specified for the ductwork system to which they are installed.

Classes A, B and C are used to signify the leakage performance of the damper casing with the respective testing method illustrated and specified in BS/EN1751.

In order to apply the square meterage leakage calculation as detailed in the standard, the reference casing area shall be taken as the perimeter size of the damper multiplied by an equivalent length of one metre, for example an 800 mm x 400 mm duct damper shall have a surface area for casing leakage performance calculated as follows: [(2 x 0.8) + (2 x 0.4)] x 1 = 2.4m² casing area.

## Location

The effective formed barrier of the damper assembly shall be located within the structural opening. Where this is not possible the section of the casing outside a fire barrier must have a fire resistance not less than that of the fire barrier and be adequately supported/protected against the possibility of displacement/damage by impact.

## Provision for Expansion

Damper assemblies generally include built-in clearance frames to meet the requirement that the casing be free to expand in the event of fire. The integrity of the fire barrier is maintained either by metal to metal contact or by fire resistant packing. Acceptable arrangements are shown in Figure 29.

## Installation

Damper installation shall be in accordance with the manufacturer's recommendations and the impending HVCA Publication DW/TM3 - Guide to Good Practice, for the design for the installation of Fire and Smoke Dampers and any conflict between the two should be resolved and authorised by the designer responsible for the fire damper selection.

# Smoke Dampers

## General

Smoke dampers shall be constructed in such a manner as to restrict the spread of smoke and other products of combustion from one occupied space to another. The blade(s) shall overlap each other and/or include edge seals. The blade(s) shall be arranged to minimise the leakage of smoke. If degradable seals are fitted, care should be taken to establish the temperature range of the material used to ensure performance compatibility. The smoke damper shall be able to operate in either or both the vertical and horizontal planes and close against dynamic air conditions.

## Types of Smoke Damper

Smoke dampers of various types are available for specific purposes, as follows:

### Single Blade

Single blade dampers shall consist of a blade of smoke tight material held in either the open or closed position by a mechanical linkage releasing to close or open and seal against the damper case. The blade shall be mechanically connected to the actuator (electric or pneumatic) and shall be triggered by interfacing with a smoke detector or fire control panel.

### Multi-Blade

Multi blade dampers shall consist of blades of smoke tight material including the blade to blade seals, where fitted. The blades shall be mechanically linked to an actuator (electrical or pneumatic) to hold the blades in either the open or closed position. The actuator shall interface with a smoke detector or fire control panel and shall be so designed as to hold the blades close against the smoke seals, where fitted.

## Materials and Construction

The damper shall be constructed from steel, stainless steel, other material or composite material with blades fitted to reduce the leakage of smoke and hot gases when the blades are in the closed position. Steel products shall be protected against corrosion and assembled in a fully finished condition as specified by the designer, in some circumstances controls may be supplied separately.

## Air Leakage

Smoke damper casings shall be as in “Air Leakage”.

## Installation

Damper installation shall be as in “Provision for Expansion” and “Installation”.

# Combination Smoke and Fire Dampers

## General

Combination smoke and fire dampers are required in air distribution systems to prevent the spread of smoke and hot gases from the fire zone and to maintain the integrity of a fire rated structure for a period compatible with that of the separating structure. They shall be tested and rated to BS476 Part 20 and 22. Reference maybe made to BS5588 Part 4 for specific smoke rating requirements.

The closure of the fire damper under action of the thermal release element shall override all other subsequent signals.

## Types of Combination Smoke and Fire Damper

Combination smoke and fire dampers of various types are available for specific purposes, as follows:

### Single Blade

Single blade combination smoke and fire dampers shall consist of a single pivoted blade contained within a fire resistant case.

The blade shall be released from its open position by means of either a thermal release mechanism rated at 72°C ± 4°C, or in addition operated by the force applied from electrical solenoid(s), electro-magnet(s), electrical/pneumatic actuator or other device.

The combination smoke and fire damper shall be able to operate in either or both the vertical and horizontal planes and close against dynamic air conditions.

### Multi-Blade

Multi-blade combination smoke and fire dampers shall consist of a series of blades mechanically linked and connected to a damper actuator with manual, electric or pneumatic opening and spring loaded closure contained within a fire resistant case.

The blades shall be released from their open position by means of either a thermal release mechanism rated at 72°C ± 4°C, or in addition operated by the force applied from electrical solenoid(s), electro-magnet(s), electrical/pneumatic actuator or other device.

The combination smoke and fire damper shall be able to operate in either or both the vertical and horizontal planes and close against dynamic air conditions.

## Materials and Construction

The combination smoke and fire damper case shall be constructed from steel, stainless steel, other material or composite material with compressible side seals fitted between the blade ends and the casing to reduce the leakage of hot gases when the blades are in the closed position.

Steel products shall be protected against corrosion and supplied in a fully finished condition as specified by the designer.

## Air Leakage

Damper casings shall be as in “Air Leakage”.

## Installation

Damper installation shall be as in “Provision for Expansion” and “Installation”.

# Internal Duct Linings

## General

Where an acoustic or thermal lining to ductwork is specified it should preferably be fitted at works. Before duct manufacture it should be clarified that specified external duct dimensions allow for the lining thickness. Any form of lining should have fire characteristics having minimum Class 0 rating and must be specified by the Designer for material type thickness, and application method.

## Lining Application Considerations

Prior to the application of any lining the internal duct surface must be thoroughly cleaned to provide a dust free dry surface which may additionally be degreased.

Securing the lining to the internal duct surface can be achieved in several ways including applied adhesive, self adhesive and physical methods such as fasteners in conjunction with surface washers at a specified square pitch.

Adjacent sections of lining should abut with minimal gap and integral or separate surface finish lap to such joints and or gap filling proprietary products being applied. This procedure is to obviate any particle migration.

During application and any curing, consideration should be given to ambient temperature and humidity requirements.

In all circumstances linings should be fitted to material manufacturer's recommended methods.

## Circular Ducts

Lining circular ducts is impractical and is not recommended.

## Cleaning and Maintenance

Designers should be aware of the possible porous/fibrous surface nature of linings as they may present practical/hazardous problems in cleaning and maintenance. Reference in this respect should be made to the following HVCA Publications:

- DW/TM2 Guide to Good Practice, Internal Cleanliness of New Ductwork Installations.

- TR17 Guide to Good Practice, Cleanliness of Ventilation Systems.

# Thermal Insulation

The provision and application of thermal insulation to ductwork is not normally the responsibility of the ductwork contractor.

Where ductwork is required to be pre-insulated, the specification should be agreed with the designer.

Where the temperature of the air within the duct is at any time low enough to promote condensation on the exterior surface of the duct and cause moisture penetration through the thermal insulation, vapour sealing may be called for, and in this case the most important requirement is to limit, penetration of the seal.

The extent of any vapour sealing of ductwork thermal insulation and the support method to be used must be clearly specified in advance by the designer.

# Standard Component Drawings and Abbreviations

The illustrations in this section not only highlight, where applicable, geometric limitations for the design and manufacture of ductwork components but also recommend standard drawing representation, terminology and abbreviations for both ductwork components and some of the more commonly used ancillary/plant items.

Designers and surveyors should note that bills of quantities should provide a full description.

Table 1 - Standard Component Drawings – Rectangular

Table 2 - Standard Abbreviations

# Self Assessment

Questions on Background Notes – Module 5.Unit 1

1.     Name three longitudinal seams.

2.    Name three cross-sectional joints.

3.    What is the extra material needed for a 6mm paned-down joint?

4.    Give five abbreviations used in ductwork.

# Answers to Questions 1-4. Module 5.Unit 1

1.

Longitudinal seams: Groove seam Pittsburgh seam – commonly known as a lock formed joint. Standing seam Single lock Snap lock

2.

Cross-sectional joint: Peine joint Slip joint Flanging Dovetail S and C cleats

3.

16mm - we use 5mm for the small piece and 11mm for the large piece. The 11mm is used with 6mm for the ledge and 5mm is knocked down around the small piece.

4.

AF Airflow VCD Volume Control Damper CFM Cubic Feet per Minute FPM Feed per Minute TA To Above FD Fire Damper HVAC Heating, Ventilation Air Conditioning AHU Air Handling Unit DIA Diameter

# Index

C

Combination Smoke and Fire Dampers, 37

Air Leakage, 39

General, 37

Installation, 39

Materials and Construction, 39

Types of Combination Smoke and Fire Damper, 37

Construction

Damper Casings, 31

Dampers used in High Pressure Systems, 30

Dampers used in Low and Medium Pressure Systems, 30

Materials, 30

Proprietary Types of Damper, 30

D

Ductwork, 21

Abbreviations used in Ductwork, 27

Allowance for Peened Joint, 25

Dampers, 27

Dovetail Seams, 22

DW/144, 27

Noise, 27

Peened Joint, 24

Slip Joints, 23

Standing Seams, 21

Ductwork:, 23, 24

F

Fire Dampers, 32

Air Leakage, 34

General, 32

Installation, 34

Location, 34

Materials and Construction, 34

Provision for Expansion, 34

Types of Fire Dampers, 32

G

General

Balancing Damper, 28

Control Damper, 28

I

Internal Duct Linings, 40

Circular Ducts, 40

Cleaning and Maintenance, 40

General, 40

Lining Application Considerations, 40

L

Lockform Machine, 12

Cross-Sectional Type, 12

Longitudinal Joint/Seams, 17

R

Regulating Dampers, 28

Construction, 30

General, 28

Installation, 31

Types of Airflow Control Damper, 28

S

Self Assessment, 48

Smoke Dampers, 35

Air Leakage, 35

General, 35

Installation, 36

Materials and Construction, 35

Types of Smoke Damper, 35

Standard Component Drawings and Abbreviations, 42

T

Thermal Insulation, 42

Types of Airflow Control Damper

Backdraft Dampers, 29

Hit and Miss Dampers, 29

Iris Dampers, 29

Multi-Blade Dampers (Single or Double Skin) Parallel or Opposed Blade, 29

Single-Blade Dampers (Single or Double Skin), 28

Slide and Blast Gate Dampers, 29

Types of Combination Smoke and Fire Damper

Multi-Blade, 37

Single Blade, 37

Types of Fire Dampers

Folding Curtain, 32

Intumescent, 33

Multi-Blade, 33

Single Blade, 32

Types of Smoke Damper

Multi-Blade, 35

Single Blade, 35